## Slide 1: Water Line Appurtenances
And their purposes

## Slide 2: Isolation Valve - Butterfly

## Slide 3: Isolation Valve – Butterfly Continued

## Slide 4: Isolation Valve – BFV Actuators
Actuators are usually what fails
  Typical safety factors
    Valve shaft: 3
    Actuator: 2
Two types:
  Worm Gear Actuator
  Traveling Nut
    Link & Lever
    Slotted Lever
Notes: All of these are quarter turn valves – worm gear, link & lever
Typical size applications
Worm gear – any size valve – suitable for large valves
Link & lever – mid range – 14-48”
Slotted lever – 12” and smaller
One advantage of a traveling nut vs a worm gear is that when you’re closing the valve the last few strokes you get a torque advantage, with worm gear 1 rotation of the nut = 1 degree, for example, but with a traveling nut it depends on where the nut is on the power screw (e.g. for the slotted lever the torque in the center would be maximum, but towards the edges of the power screw the there is a torque advantage

## Slide 5: Miter Gear vs Spur Gear vs Bevel Gear
Notes: Miter gear spur gear bevel gear
Lots of torque required to close valve, use gearing to allow turing of valve
Actuators are always self-locking. For MechE’s should remember power screws where Force of friction exerted on power screw exceeds that of turning screw.

## Slide 6: Isolation Valve – Gate Valve OS&Y
Notes: Outside Screw & Yoke vs Non-Rising Stem
OS&Y – you can see at a glance if the valve is open because the stem will be sticking out the top – common in fire protection systems
OS&Y – stem vs screw – you decide

## Slide 7: Isolation Valve – Gate Valve NRS
Notes: Outside Screw & Yoke vs Non-Rising Stem

## Slide 8: Gate vs Butterfly – Valve Selection
Cost
  Gate valves become more expensive vs butterfly valves for pipes 24” and larger.
Resilient seals
  Operational reasons may necessitate a GV in some scenarios.
Hot-Tapping
  Full port needed for tapping machine, requires gate valve.

## Slide 9: Air Valve - Air Valve

## Slide 10: Air valve - Vacuum Valve

## Slide 11: Combination Air Valve
Also sometimes called out as AI/VR (Air Intake / Vacuum Relief)
Unlikely to find a vacuum valve by itself, in almost all cases accompanied by a air relief valve
Variant of the CAV is Vent-O-Mat

## Slide 12: Control Valves – Globe Valve
Pressure reducing valve
Pressure sustaining valve
Pressure relief valve

## Slide 13: Control Valves – Ball Valve

## Slide 14: Control Valves – Plug Valve
Isolation or throttle
3 or 4-way valves available
Not typical for potable water
Notes: Typical for slurrys or fluids with sediments such as sewage or raw water

## Slide 15: Actuators – Ball & Plug
Actuators used for BFVs also apply here.

## Slide 16: Access Manway
Every 1000 ft
Each end of tunnels
Each side of isolation valve

## Slide 17: Air valve – Manhole

## Slide 18: Drainline Manhole
Drains water line by gravity
Will be at a low point along the line
Usually only used if can connect hydraulically to a storm sewer or channel
Uncommon

## Slide 19: Butterfly Valve – Manhole/vault
Manway – Valve - Manway

## Slide 20: Valve Box

## Slide 21: Fire Hydrants
Typical configuration
  Gate valve to isolate

## Slide 22: Coatings
Typical coatings for water line appurtenances is to meet AWWA C550
  AWWA C550 - PROTECTIVE INTERIOR COATINGS FOR VALVES AND HYDRANTS
    NSF 61 certified
  Hydrants, air valves, isolation valves and other cast appurtenances
    Typical to see epoxy coating
      Epoxy
        Fusion Bonded
        Liquid Epoxy
  Polyurethane
    Sometimes used as an interior coating for hydrants vs epoxy
Notes: Both epoxies are thermo-set
fusion bonded is a sprayed powder that’s applied to a heated component that melts it to the component
Liquid epoxy is the 2-part spray epoxy (can also be brushed)
Fusion epoxy – cheaper – very short cure time (liquid epoxy is 5 to 10 days - less impact/abrasion resistance – difficult to field apply – no VOCs (high solids liquid epoxy is not releases VOCs, but fewer than solved based coatings (e.g. enamels)).
Fusion bonded epoxy looks similar to

## Slide 23: Cathodic Protection – Anode & Rectifier

## Slide 24: Cathodic Protection – Isolation & bonding

## Slide 25: Cathodic Protection – Test Stations
Cased crossing
Potential

## Slide 26: Instrumentation Not typically seen outside of plants
Flow Meters
  Mag meter
    Insertion
    Full Port
  Differential Pressure
    Venturi
    Orifice plate
  Service Meters
    Nutating Disc
    Turbine Meter
    Ultrasonic
    Mag Meter
Pressure Sensors