## Slide 1: Pipe Joints – Steel Pipe

## Slide 2: Main Type of Unrestrained Joints
  Bell and Spigot Rubber Gasketed Joint
  Unrestrained Bolted Steel Coupling
  Unrestrained Bolted Split-Sleeve Coupling
  Permalok (Steel Casing)

## Slide 3: Bell & Spigot Joint
  Easy to Assemble, Self Centering, Economical
  Allows Joint to be offset to create long-radius curves
  Typically only suitable to Pipes <= 72 inches
  Unrestrained. Should not be used in areas subject to thurst (elbows, tees, valves, dead-ends)
  https://youtu.be/rSQLSOkJnY0?t=40

## Slide 4: Bolted Sleeve Coupling (1)
  This type of couplings are used for:
    Relive stresses on pipe due to small amounts thermal expansion or differential settlement
    Joining plain-end pipe to flange adapters
    Jointing pipe of different diameter or materials
  Axial movement of pipes allowed through the shearing of the rubber gasket
  Not intended for application where pipe will experience shear or bending moments

## Slide 5: Bolted Sleeve Coupling (2)

## Slide 6: Bolted Split-Sleeve Coupling (1)
  Clamp-like joint couplings used to:
    Allow some lateral movement of the pipe due to settlement
    Allows some axial movement (1/2”) to relieve stresses on pipe due to thermal contraction or expansion
  Easier to install and more flexible than bolted steel coupling
  Not intended for application where pipe will experience shear or bending moments

## Slide 7: Bolted Split-Sleeve Coupling (2)

## Slide 8: Steel Casing - Permalok
  Interlocking Joint is not design to handle internal pressure, therefore most often used in Casings
  Installation is similar to bell and spigot in that be it only requires the both ends of the pipe to be joined together
  Joint eliminates the need to field weld casing
  Different types of joints exists for different application (HDD, pipe jacking, ect)

## Slide 9: Main Type Restrained Joints
  Field Welded Joint
  Flanged Joint
  Mechanical Joint
  Bolted Sleeve Coupling
  Bolted Split-Sleeve Coupling
  Grooved and Shouldered Coupling
  Mechanical Slip Expansion Joint

## Slide 10: Field Welded Joint (1)
Lap-Welded Joint
  Restrained Joints created by expanding one side of a pipe (bell) and inserting a plain end (spigot)
  Pipe are secured with either an internal or external, or both depending on diameter, circumference fillet weld equal to thickness of pipe
  Most common restrain joint type for Steel
  Allows Joint to be offset up to 2-3 degrees by pulling joint
  With join installed, a heat-shrink sleeve is install around the exposed pipe
  https://www.youtube.com/watch?v=iVs5FvvqPl0

## Slide 11: Field Welded Joint (2)
Butt-Strap Joint
  Restrained Joint
  Often used for field adjustments
  Allows for a gap to exist between two pipe pieces

## Slide 12: Field Welded Joint (3)
Butt-Welded Joints
  Both pipes needs to be plain ends or bevel ends.
  Typically, both pipes needs to have similar wall thickness
  Full penetration weld required
  https://youtu.be/dkASZEm1RZ4?t=10

## Slide 13: Flanged Joints
  Used at location that will require future disassembly of joint for maintenance
  For flanges to properly seal, both ends need to be parallel, and property aligned
  3 main components of a flange:
    Flange – fabricated ends of pipe with pre-made holes
    Fasteners – bolts, nuts and washers that create the axial load to seal the joint
    Gasket – deformable joint that seals joint and makes it watertight.
  All components must be design to withstand the environment where they are on.

## Slide 14: Restrained Bolted Sleeve Coupling
  In order to restrained a bolted sleeve coupling, an external harness is needed with rods that prevent pipe from slipping out.
  Allows some axial movement without pulling the pipe joint

## Slide 15: Restrained Bolted Split-Sleeve Coupling
  Restrained Bolted Split-Sleeve coupling utilize a ring that is welded to each pipe. The coupling straddles these restrained rings and resist axial thrust
  No need for an external harness
  Allows some axial movement without pulling the joint.

## Slide 16: Grooved and Shouldered Coupling
  Used with pipe that comes pre-manufactured with grooves on either end. A gasket is wrapped around pipe ends, housing sits inside the pipe grooves and bolts are used to tighten joint together
  Coupling used when limited angular movement on pipe is desired while still restraining the pipe joint

## Slide 17: Mechanical Slip Expansion Joint (1)
  Used when large axial movement is anticipated in pipe due to thermal expansion/contractor or other factors
  Joint can be provided with limiting rods that restrain the amount of movement the pipe can do
  The Initial Slip-pipe position is established before installation based on pipe length, temperature changes

## Slide 18: Mechanical Slip Expansion Joint (2)
  Need to material and coating of segment of joint that slides back and forth. In marine environments, stainless steel is often the only choice available.

## Slide 19: Electrical Insulation
  Long section of pipe can conduct electric currents from difference in ground potentials or stray currents. Long section of steel pipe often need to be separated into sections that electrically insulated
  When connecting Steel Pipe to Cast Iron, Ductile Iron, Concrete Pressure Pipe need to provide an electrically insulated joint. This allows the cathodic protection system of both pipe to function independently.
  Insulation can be done by installing insulating gaskets, sleeves or washers. Insulated couplings can also be used.